## 1. Intro
FIRE PROTECTION SYSTEMS INSPECTION, TESTING, MAINTENANCE, AND REPAIR BID NUMBER H080-26
Request for Proposal
Appendix C
Scope
This Request For Proposal will cover the inspection, testing, maintenance, and repair of the water based/other fire protection systems. This includes, but is not limited to, the following:
Equipment |  |  | Count
Electric fire pumps |  |  | 13
Pre-action systems |  |  | 20
Control valves and flow switches |  |  | 3000
Foam cannon |  |  | 1
Sapphire |  |  | 1
Standpipes |  |  | 47
Fire water storage tank |  |  | 1
Dry valve systems |  |  | 25
Backflows |  |  | 55
UAB is seeking bids from qualified contractors to provide inspection, testing, maintenance, repairs of Fire protection systems at UAB Medicine, which consist of 25 or more research, acute-care hospital, and other healthcare environment buildings that hold dry and wet fire protection systems, in accordance of applicable NFPA, state, and local authority having jurisdiction (AHJ), manufacturer recommendations, and healthcare requirements. The term of this requirement is intended to consist of a three (3) year agreement to renew the agreement, with the option to renew under the same terms and conditions as originally agreed upon, for two (2) additional one (1) year periods.
https://www.uab.edu/financialaffairs/doing-business/electronic-bid-bulletin-board
Section | Section Title | Instructions
1 | Intro | This is an introduction/outline of Appendix C of the RFP.
2 | Timeline | Review and Understand
3 | Key | Please refer to this key when reviewing and filling in each section.
4 | Vendor Contact Info | Provide the contact information for a single company representative as instructed.
5 | UAB Requirements | Provide responses and comments as applicable for each section as instructed.
6 | Questionnaire | Provide responses and comments as applicable for each section as instructed.
7 | Implementation Timeline | Please provide an implementation timeline as instructed in this section.
8 | References | Provide references where work of a similar size and nature was performed within the last five (5) years.
9 | Pricing | Fill in this section with proposed pricing. A formal quote must also accompany your RFP submission.
10 | Agreements | Part 1: Review section 3.2(d) of the Request for Proposal and attach any required agreements.
12 | Value Adds | Review section 3.2c of the Request for Proposal and attach any additional Value Add propositions.
Other:
13 | Customer Facilities | This is a listing of UAB Hospital facilities and area by location included in the RFP.
14 | Required Documents | This is a list of documents that are required with your RFP submission.
Please return this Request for Proposal by close of business on the date specified in the Timeline. It is the responsibility of the vendor to ensure that their bid response is received in Hospital Purchasing Department by the opening date/time specified in the Timeline, regardless of the mailing method.

## 2. Timeline
RFP TIMELINE
# | ACTION | OWNER |  | TIME
1 | Issue RFP | UABHS | 2026-01-05 | 5:00 PM CDT
2 | Intent to Bid Deadline | Vendor | 2026-01-12 | 5:00 PM CDT
3 | Mandatory Walkthrough / Facility Tour | UABHS/Vendor | 2026-01-16 | 10:00 AM CDT
4 | Deadline for Formal Questions | Vendor | 2026-01-23 | 5:00 PM CDT
5 | Response to Questions Issued | UABHS | 2026-01-28 | 5:00 PM CDT
6 | Proposals Due to UAB | Vendor | 2026-02-05 | 5:00 PM CDT
7 | RFP Opening | UABHS | 2026-02-06 | 3:00 PM CDT
8 | Vendor presentations - optional | Vendor
9 | Supplier Selection (not a hard deadline) | UABHS | 2026-02-18 | 5:00 PM CDT
10 | Contract Go-Live (estimated) | UABHS/Vendor | 2026-04-01 | 5:00 PM CDT
***Dates are subject to change at UAB's discretion.
Locations for Mandatory Walkthrough / Facility Tours:
UAB Hospital
Address: | Jefferson Tower Room 323 (3rd Floor)
619 19th Street South
Birmimgham, Alabama 35249
Please meet in Jefferson Tower, Room 323 at the date and time specified in the Timeline above.
The UAB Hospital Facility Tour will include three (3) locations. Please see the Facility Tour Schedule below for meeting dates, times and locations. The address for UAB Highlands is listed in the Facilities section. Please meet in the main lobby of UAB Hospital Highlands at the specified times.
Other Information
We wil be on foot during the facility tour, so please wear comfortable shoes.
Please review section 2.2(b) of the RFP for more information regarding visitor and masking policies.
UAB team members will provide general information during the facility tours, but questions will need to be emailed to the buyer email address listed in the RFP by the Deadline for Formal Questions specified in the Timeline.
UAB will not be providing lunch during the walkthroughs, but time has been allotted for lunch. Please plan accordingly.
FACILITY TOUR SCHEDULE
|  | LOCATION | DATE | TIME
MEET AT JT323 FOR UAB HOSPITAL TOUR |  | UAB HOSPITAL - MAIN | 2026-01-16 | 8:00
TOUR MAIN HOSPITAL |  | UAB HOSPITAL - MAIN | 2026-01-16 | 9:00
FREE TIME FOR LUNCH |  | N/A
MEET AT UAB HOSPITAL- HIGHLANDS |  | UAB HOSPITAL - HLND | 2026-01-16 | TBD
TOUR UAB HOSPITAL - HIGHLANDS |  | UAB HOSPITAL - HLND | 2026-01-16

## 3. Key
Key
Please refer to this key when reviewing and filling in each section.
Vendor Response Code Key:
S - Standard to Offering | The requirement/specification is standard to the system/product or service offering and does not require an additional fee or subscription.
N - Not Available | The requirement/specification is not available.
Priority Code Key:
R - Required | This is a required specification for the RFP.

## 4. Vendor Contact Info
VENDOR CONTACT INFORMATION
Please provide the contact information for a single reperesentative within your company for this RFP
Vendor Name | Company Address | First Name | Last Name | Phone Number | Email Address

## 5. UAB Requirements
UAB Requirements
Directions: Please note whether you have complied with the listed specifications in your formal proposal by choosing a response in the drop-down menu in column E. Refer to Section 3 of Appendix C for explanation of each response. Please provide comments as requested. If you select "Not Available (N) " on any response, you must provide an explanation in column E. Please answer each section individually and concisely. Do not refer to another section's comments.
# | Requirement | Priority Code | Vendor Response Code | Vendor Comments
General
1 | Contractor will complete annual fire sprinkler system inspections and routine maintenance in accordance with NFPA 25 and the State of Alabama | R - Required
2 | Contractor will provide a signed/certified report of inspection to UAB in a timely manner. | R - Required
3 | Contractor will be allowed to make minor repairs or changes to the system with oversight from UAB. If minor faults requiring repairs are discovered, Contractor should address them and include the service work in the invoice. | R - Required
4 | As part of every complete annual inspection, the Contractor will survey the building and fire sprinkler systems (and all related equipment) for any manufacturers’ recalls, recommended repairs, upgrades, or modifications. | R - Required
5 | Contractor shall maintain the systems as hereinafter specified and shall provide all labor and materials necessary to keep the systems properly maintained for correct, efficient operation at all times. | R - Required
6 | Contractor shall provide, at its own expense, all necessary licenses, permits, or other authorization required by all applicable regulatory agencies. | R - Required
7 | Contractor shall not shut down any equipment and systems without coordinating with UAB Hospital Maintenance personnel as appropriate. | R - Required
8 | Contractor must maintain a sufficient quantity of common spare parts to provide prompt repairs. If a delay in repairs occurs due to lack of parts, the contractor shall promptly notify the university and may be responsible for the costs of special fire watches until such time repairs are completed. In addition, if in the opinion of the University, parts delays cause unacceptable problems, the University reserves the right to make direct part purchase from other sources. Contractor can also access UAB's warehouse if needed for parts. | R - Required
9 | To maintain the integrity of the systems, only parts made by the original manufacturer or other authorized replacement parts by the manufacturer will be an acceptable replacement. Parts are to be installed in accordance with manufacturers’ written recommendations. | R - Required
10 | During the period of the contract or any extension thereof, UAB reserves the right to add or delete specific services and/or locations in the prevailing contract process. UAB will give seven (7) day notice to the vendor of requested changes. | R - Required
11 | Contractor must supply UAB with all warranty information whether expressed or implied. | R - Required
12 | Contractor will take adequate precautions to protect all surfaces. The vendor(s) will repair any damage caused because of inspection or servicing of equipment including abuse, misuse, and neglect. | R - Required
13 | Contractor is responsible for properly disposing of any materials removed or replaced. In addition, any areas disturbed should be restored to their original condition. | R - Required
14 | Contractor shall comply with all laws or ordinances and all rules and regulations of health, public and /or other authorities controlling or limiting the methods, the materials to be used or the actions of those engaged in work of this kind. | R - Required
15 | Contractor shall have ICRA Containment knowledge and meet the requirements | R - Required
16 | Guarantee: The awarded vendor(s) shall fully guarantee all workmanship and parts furnished and installed under this contract against defect for six (6) months after completion. Defects will be repaired or replaced at no charge to UAB. | R - Required
17 | UAB reserves the right to cancel this contract at any time upon thirty (30) days’ written notice to the contractor. | R - Required
18 | Contractor will utilize UAB computerized maintenance management system to enter minor repairs | R - Required
19 | Contractor must be able to service all facilities and equipment within 30 days after contract award | R - Required
Documentation & Reporting
20 | NFPA-compliant inspection reports | R - Required
21 | Deficiency reports clearly categorized by severity | R - Required
22 | Electronic reports; i.e.PDF, Word documents, Excel | R - Required
23 | Documentation suitable for CMS, Joint Commission, and AHJ surveys | R - Required
24 | Retention of records for minimum of 5 years | R - Required
Regulatory & Code Compliance
25 | All services must comply with: NFPA 25 – Water-Based Fire Protection Systems, NFPA 72 – National Fire Alarm and Signaling Code, CMS Conditions of Participation, Joint Commission Life Safety (LS) & Physical Environment (PE) Standards, and State and Local Fire Codes | R - Required
Deficiency Identification & Repair
26 | Contractor shall document all deficiencies using NFPA-compliant terminology | R - Required
27 | Separate ITM findings from repair recommendations | R - Required
28 | Provide cost estimates within 1 business day upon request | R - Required
Staffing
29 | The technician or mechanic to perform the annual testing shall be licensed by the State of Alabama in fire protection. | R - Required
30 | The contractor is required to have NICET fire protection/building systems certification | R - Required
31 | Contractor shall use trained personnel directly employed and supervised by the contractor to examine, adjust, repair, and test the systems regularly and systematically. | R - Required
32 | Contractor shall not subcontract any part of this contract without written, prior approval from UAB Management | R - Required
33 | Contractor must have a minimum of 5 years’ experience. | R - Required
34 | Contractor shall not sell, transfer, assign or otherwise dispose of this contract to any third party for the performance of their work. Exceptions are services outside their normal expertise such as excavation. All subcontractors must be approved prior to the start of work by UAB Management. | R - Required
35 | Contractor’s personnel shall observe all rules and regulations and policies in effect at UAB. | R - Required
36 | Contractor’s motorized vehicles shall be identified with the company’s name and/or logo in clear view. | R - Required
37 | Contractor’s personnel shall be in uniform, and dress shall be professional attire that abides by UAB Hospital dress code. UAB designed badge must always be displayed. | R - Required
Schedule
38 | All inspections and testing must be coordinated and scheduled through UAB Hospital Maintenance Management. | R - Required
39 | Work shall be performed mostly during normal working hours. Normal working hours are defined as 5:00 a.m. to 5:00 p.m. Monday through Friday, with exceptions to e.g. Pump Runs, Annual Testing, and as needed. | R - Required
Fitter requirements
40 | Vendor must provide a fitter, on an as needed basis, for 208 hours a year for emergency purposes or to repair what UAB is requesting to use the time for (26 days a year) | R - Required
41 | Perform and abide by all Joint Commission & compliance requirements, AL State requirements, AHJ | R - Required
Technology Requirements
42 | Vendor must be able to provide & store all inspection and testing reports electronically to UAB, at least 5 years | R - Required
43 | Deficiency reports are required to include the following: code reference, photo, and recommendation to correct deficiency | R - Required
44 | Required inspection & testing documentation is to be provided to Hospital Maintenance immediately upon completion | R - Required
45 | Required to use UAB Computerized Maintenance management system | R - Required
Emergency Response Times
46 | Emergency / System Impairment response time must be within 2 hours of call | R - Required
47 | Urgent Deficiencies / Inspection Failures within 24 hours | R - Required
Detailed requirements for Wet Systems Annual Inspection
48 | Inspect the wet systems and risers | R - Required
49 | Perform drain test and record static and residual pressure(s) | R - Required
50 | Determine if the fire sprinkler system is functional and in satisfactory condition. | R - Required
51 | Check condition of drain valves, gauges, and related components. | R - Required
52 | Inspect and test all sprinkler control valves for proper position and condition. | R - Required
53 | Tag alarm valves as required by code and law. | R - Required
54 | Inspect sprinkler control valve identification signs and security arrangements. | R - Required
55 | Check all control valves: Function check system control valves and sectional valves and lubricate as necessary. | R - Required
56 | Check condition of all alarm valves and related trim | R - Required
57 | Check the condition of sprinkler heads for any obstructions or coatings. | R - Required
58 | Check reserve sprinkler heads for proper supply and arrangement. | R - Required
59 | Check for adequate clearance around sprinkler heads for proper water distribution. | R - Required
60 | Check general condition of sprinkler system piping, hangers, and related equipment. | R - Required
61 | Test water motor alarm gong on all systems by: Operating inspectors test connection, Visual inspection, Water flow for evidence of any obstruction, Inspect and test sprinkler alarm system component. | R - Required
62 | Inspect the following fire department connections: Couplings, Caps, Threads, Clapper, Check valves, Drains, Lubricate as necessary | R - Required
63 | Instruct designated individuals in the care and maintenance of the fire protection equipment as required by NFPA 13 and 25 State requirements and University’s insurance requirements. | R - Required
64 | Dry-trip valve to determine if it is in service and in working condition. | R - Required
65 | Check drain valves, gauges, and related components. | R - Required
66 | Inspect and test all control valves for proper position, condition, and accessibility | R - Required
67 | Tag dry valve | R - Required
68 | Check sprinkler heads for any obstruction/coatings that may hinder activation. | R - Required
69 | Check the condition of dry valve and related trim | R - Required
70 | Check reserve sprinkler heads for proper supply and assortment. | R - Required
71 | Check for adequate clearance around sprinkler heads for proper water distribution. | R - Required
72 | Drain low points per NFPA 25 | R - Required
73 | Inspect pressure-reducing valve per manufacturer standards and report as necessary. | R - Required
Detailed requirements for Fire Pump Inspection
74 | Perform fire pump performance test in accordance with NFPA Annual Pump test | R - Required
75 | Test all fire pump functions for satisfactory performance. | R - Required
76 | Check all valves to make sure they are fully open. | R - Required
77 | Test operation of pressure and casing relief valve | R - Required
78 | Inspect packing glands; adjust as necessary. | R - Required
79 | Check fire pump start – stop pressures; adjust as necessary. | R - Required
80 | Test pump for proper operation and conditions | R - Required
81 | Inspect bearing for proper operation and condition. | R - Required
82 | Provide a pump curve showing the operation of the pump as required by NFPA | R - Required
83 | Conduct routine maintenance as recommended or required by NFPA | R - Required
Detailed requirements for Backflow Preventers - Annual Inspection
84 | Perform annual inspection on backflow preventers in accordance with city water and Fire & Domestic departments. | R - Required
85 | Upon completion of the inspection, documentation will be forward to the UAB stating that the backflow preventer has been tested and inspected in accordance with manufacturer’s recommendation and Water Authority Jurisdiction | R - Required
Documentation
86 | Perform annual inspection on backflow preventers in accordance with city water and Fire & Domestic departments. | R - Required
87 | Upon completion of the inspection, documentation will be forward to the UAB stating that the backflow preventer has been tested and inspected in accordance with manufacturer’s recommendation and Water Authority Jurisdiction | R - Required
Rates and Billing
88 | Contractor must assign an accounting/financial representative for invoicing and all fiscal responsibilities and correspondence. The following is required for invoice and payments: | R - Required
Invoice Date & Invoice Number & UAB FSI Work Order Number
Bill & Remit-to address. Name of UAB requester
Dates of billing cycle
Labor and Non-Labor costs
Name of technician (s)
Number of hours worked by each technician.
Type of Labor Rate billed.
Description of work performed each day with Building name and location.
If non-labor costs, description of items purchased, and cost of items.
Standard payment term net 30 days from date of invoice
Travel time is not billable.
89 | Invoices for non-routine work must be supplied withing 5 business days of work completion | R - Required
Note on E5: Vendor Response Code Key: S - Standard to Offering N - Not Available

## 6. Questionaire
QUESTIONAIRRE
Directions: Please review the questions in column C and provide your response as requested in Column D. We also ask that if you answer "No" on any response that you provide your reason for being unable to comply/respond. Please answer each section individually and concisely. Do not refer to another section's comments (ex: do not write "please refer to the response for Battery powered mobile units").
# | Question | Vendor Comments
1 | Provide a brief overview of your company’s history. Include the year business was founded, number of employees, locations, number of years offering/supporting the proposed solution.
2 | How many customers do you currently have utilizing the services proposed in your RFP submission?
3 | What differentiates your company from other companies in the industry?
4 | Describe your plan for measuring, monitoring and enhancing customer satisfaction.
5 | Describe your experience performing in accordance with Federal, The Joint Commission, State and other local laws and regulations.
6 | Will dedicated technicians be assigned to this Facility? Explain.
7 | Describe your impairment management process in a healthcare environment.
8 | Describe how you support Interim Life Safety Measures (ILSM).
9 | If selected, how quickly will you be able to provide/implement services?
10 | Are there any facility requirements that UAB will need to provide? If yes, please list these in the vendor comments.
11 | Does your company have any pending mergers and/or acquisitions that could change your business model.
12 | Describe your firm’s understanding of being flexible regarding short notice, off-hours, to meet UAB's needs for providing the products / services detailed in the RFP. Include in your description the ability to work during non-normal business hours (after 5 pm Monday – Friday and weekends).
13 | Years of experience serving healthcare facilities (acute care, ambulatory, behavioral health, etc.).
14 | Number of healthcare campuses currently under contract.
15 | Describe experience working in 24/7 occupied hospital environments.
16 | Describe technician training related to infection control, ILSM, and healthcare safety.
17 | Confirm ability to comply with Facility policies, including ILSM and infection control.
18 | Do you have any previous work history with UAB ?
19 | Does your service department operate within a 50-mile radius of UAB?
20 | Do you have dispatchers available 365/24/7, including holidays?
21 | Is your contact service available 365/24/7, including holidays?
22 | Describe any contracts terminated for cause in the last five years.

## 7. Implementation Timeline
Implementation Timeline / Transition Plan
Transition in 30 days after award to coordinate closely with Hospital Maintenance to prevent ITM gaps, Assume responsibility for all upcoming Inspections, Testing, and Maintenance (ITM) frequencies upon contract start, Review and incorporate prior inspection records and deficiency histories (if applicable), Validate open deficiencies and impairment statuses, Conduct joint field walkthroughs (as requested), Ensure uninterrupted fire protection system readiness during transition

## 8. References
References
Instructions: Provide at least three (3) references where work of a similar size and nature was performed within the last five (5) years.
Reference/ Facility Name | Contact Name | Contact Title | Phone Number | Email Address | Hospital Bed Count | Nature of Work

## 9. Pricing
Pricing
Instructions: Please fill in this section with proposed pricing. You may add additional fees as required under the Other Fees." A formal quote must accompany your RFP submission.
Item Description | Price
Inspector Hourly labor rates (regular, first 40 hours in work week)
Inspector Hourly labor rates (weekend/after-hours/OT, excess of 40 hours)
Pipefitter Hourly labor rates (regular, first 40 hours in work week)
Pipefitter Hourly labor rates (weekend/after-hours/OT, excess of 40 hours)
Markup on Materials (%)
Other:

## 10. Agreements
AGREEMENTS
Please review section 3.2d of the Request for Proposal. Vendor must provide a copy of any End-User agreements that will be required before implementation with RFP submission.
Question | Vendor Response | Comments
Do you require any additional documentation (Agreements, etc.) to be signed by UAB?

## 12. Value Adds
VALUE ADDS
Please review section 3.2c of the Request for Proposal and insert any Value-Add proposals here.

## 13. Customer Facilities
Customer Facilities
Site | Site Description | Facility | Facility No. | Facility Name | Net Assignable Square Feet | Net Usable Square Feet | Gross Square Feet | Active
LEASED | UAB LEASED SPACE | 405 | 0497 | 405 BUILDING | 1294 | 1294 | 1294 | Y
LEASED | UAB LEASED SPACE | 410B | 0495 | 410 B BUILDING | 20799.31 | 24345.54 | 25753.54 | Y
LEASED | UAB LEASED SPACE | 450A | 0507 | 450A BUILDING | 4946.86 | 5538.1 | 5991.1 | Y
LEASED | UAB LEASED SPACE | 508 | 0414 | 508 BUILDING | 22654.88 | 23801.52 | 25781.52 | Y
LEASED | UAB LEASED SPACE | 530 | 0496 | 530 BUILDING | 19933.45 | 20827 | 23021 | Y
LEASED | UAB LEASED SPACE | 916 | 0418 | 916 BUILDING | 2504.66 | 3324.81 | 3815.81 | Y
LEASED | UAB LEASED SPACE | 1110 | 0437 | 1110 BUILDING | 1331.22 | 1712.92 | 2142.92 | Y
LEASED | UAB LEASED SPACE | 1701 | 0352 | 1701 BUILDING | 2648.47 | 3849.41 | 4375.41 | Y
LEASED | UAB LEASED SPACE | 1874 | 0522 | 1874 BELTLINE ROAD | 0 | 0 | 0 | Y
LEASED | UAB LEASED SPACE | 2221 | 0482 | 2221 BUILDING | 9725.84 | 9853.75 | 10244.75 | Y
LEASED | UAB LEASED SPACE | 2300 | 0431 | 2300 BUILDING | 18035.9 | 19325.04 | 20962.04 | Y
LEASED | UAB LEASED SPACE | 3100 | 0499 | 3100 BUILDING | 13243.17 | 13703.23 | 14157.23 | Y
LEASED | UAB LEASED SPACE | 3307 | 0502 | 3307 BUILDING | 19454.98 | 21554.01 | 22271.01 | Y
LEASED | UAB LEASED SPACE | EFH | 0036 | CALLAHAN EYE HOSPITAL HEALTH CARE AUTHORITY | 122492.24 | 202147.45 | 238260.45 | Y
LEASED | UAB LEASED SPACE | ACC | 0265 | CHILDRENS AMBULATORY CARE CENTER | 49194.73 | 52255.05 | 99024.05 | Y
LEASED | UAB LEASED SPACE | CHB | 0357 | CHILDRENS HOSPITAL HARBOR CENTER | 32216.9 | 56677.22 | 63619.22 | Y
LEASED | UAB LEASED SPACE | CHT | 0018 | CHILDRENS HOSPITAL TOWER | 22456.7 | 26988.69 | 71450.69 | Y
LEASED | UAB LEASED SPACE | CRM | 0422 | CRAMER HALL | 156 | 156 | 156 | Y
LEASED | UAB LEASED SPACE | DEW | 0491 | DEWBERRY BUILDING | 32051.87 | 45097.65 | 69472.65 | Y
LEASED | UAB LEASED SPACE | HCSMT | 0508 | HEALTH CENTER SOUTH MEDICAL TOWERS | 5508 | 5508 | 5508 | Y
LEASED | UAB LEASED SPACE | IVNS | 0268 | HEALTH CLINIC INVERNESS | 4148.95 | 5782.13 | 6423.13 | Y
LEASED | UAB LEASED SPACE | HTA | 0503 | HIGHLANDS TRAIL APARTMENT | 1000 | 1000 | 1000 | Y
LEASED | UAB LEASED SPACE | IDB | 0408 | INNOVATION DEPOT | 2350 | 2350 | 2350 | Y
LEASED | UAB LEASED SPACE | JCDHM | 0455 | JEFFERSON CO DEPT OF HLTH - MIDFIELD | 1701 | 1701 | 1701 | Y
LEASED | UAB LEASED SPACE | JCDH | 0447 | JEFFERSON COUNTY DEPARTMENT OF HEALTH | 866.09 | 866.09 | 1200.09 | Y
LEASED | UAB LEASED SPACE | JNWB | 0339 | JOHN N WHITAKER BUILDING | 104879.96 | 163989.69 | 180913.69 | Y
LEASED | UAB LEASED SPACE | TKC | 0271 | KIRKLIN CLINIC | 193367.47 | 403763.94 | 577002.94 | Y
LEASED | UAB LEASED SPACE | ARCL | 0378 | KIRKLIN CLINIC ACTON ROAD | 16493.17 | 24476.85 | 27942.85 | Y
LEASED | UAB LEASED SPACE | KCPD | 0354 | KIRKLIN CLINIC PARKING DECK | 6831.32 | 8387.96 | 9336.96 | Y
LEASED | UAB LEASED SPACE | MAG | 0454 | MAGNOLIA BUILDING | 6832.95 | 8747.06 | 11495.06 | Y
LEASED | UAB LEASED SPACE | MOPS | 0395 | MAGNOLIA OFFICE PARK | 17652.35 | 19675.54 | 23368.54 | Y
LEASED | UAB LEASED SPACE | MT | 0133 | MEDICAL TOWERS | 70032.16 | 82353.06 | 155770.06 | Y
LEASED | UAB LEASED SPACE | MRMC | 0448 | MONTGOMERY REGIONAL MEDICAL CAMPUS | 5524 | 5524 | 5524 | Y
LEASED | UAB LEASED SPACE | MMT | 0427 | MORROW MEDICAL TOWER | 6847.02 | 11036.11 | 12702.11 | Y
LEASED | UAB LEASED SPACE | PP1 | 0416 | PARK PLACE I SOUTH | 20288.9 | 28880.72 | 36240.72 | Y
LEASED | UAB LEASED SPACE | PP2 | 0410 | PARK PLACE II NORTH | 18898.35 | 26143.56 | 34901.56 | Y
LEASED | UAB LEASED SPACE | PAUL | 0344 | PAULA BUILDING | 5876.89 | 9304.44 | 21083.44 | Y
LEASED | UAB LEASED SPACE | RRS | 0432 | RAILROAD SQUARE | 15708.17 | 19195.88 | 20857.88 | Y
LEASED | UAB LEASED SPACE | SCOM | 0504 | STURBRIDGE COMMONS APARTMENT | 1000 | 1000 | 1000 | Y
LEASED | UAB LEASED SPACE | LEEDS | 0459 | UAB MEDICINE LEEDS CLINIC | 10994.4 | 15405.17 | 17056.17 | Y
LEASED | UAB LEASED SPACE | OLB | 0456 | UAB MEDICINE OUTREACH LAB - BIRMINGHAM | 2795.58 | 4212.8 | 4762.8 | Y
LEASED | UAB LEASED SPACE | WHARF | 0484 | UAB WELLNESS, HEALTH AND RESEARCH FACILITY | 10843.92 | 16934.93 | 20502.93 | Y
LEASED | UAB LEASED SPACE | VRMC | 0391 | VAUGHAN REGIONAL MED CTR | 10182.93 | 13437.94 | 15092.94 | Y
MEDWEST | UAB MED WEST | UMWST | 0520 | UAB MEDICAL WEST HOSPITAL | 0 | 0 | 0 | Y
UABSTV | UAB ST. VINCENT'S | 744 | 6034 | 744 BUILDING | 0 | 0 | 0 | Y
UABSTV | UAB ST. VINCENT'S | 2808 | 6033 | 2808 BUILDING | 0 | 0 | 0 | Y
HOSPITAL | UAB-HOSPITAL | 176F | 0402 | 176 FACILITY BUILDING | 306438.31 | 551793.17 | 616065.17 | Y
HOSPITAL | UAB-HOSPITAL | 502 | 0372 | 502 BUILDING | 5909.43 | 8157.88 | 9027.88 | Y
HOSPITAL | UAB-HOSPITAL | 516 | 0285 | 516 BUILDING | 2737.38 | 4143.2 | 4584.2 | Y
HOSPITAL | UAB-HOSPITAL | 2020 | 0217 | 2020 BUILDING | 5444.04 | 8856.02 | 9854.02 | Y
HOSPITAL | UAB-HOSPITAL | CPM | 0235 | CENTER FOR PSYCHIATRIC MEDICINE | 115479.29 | 169806.51 | 187558.51 | Y
HOSPITAL | UAB-HOSPITAL | GSB | 0039 | GENERAL SERVICES BUILDING | 84547.47 | 117477.78 | 130400.78 | Y
HOSPITAL | UAB-HOSPITAL | HGLDPD | 0425 | HIGHLANDS PARKING DECK | 173541.04 | 175980.33 | 177463.33 | Y
HOSPITAL | UAB-HOSPITAL | HSB | 0371 | HOSPITAL SUPPORT BUILDING | 22520.05 | 39820.95 | 43384.95 | Y
HOSPITAL | UAB-HOSPITAL | IRF | 0517 | INPATIENT REHAB FACILITY | 211715.83 | 307193.09 | 340882.09 | Y
HOSPITAL | UAB-HOSPITAL | JT | 0236 | JEFFERSON TOWER | 152963.39 | 275782.29 | 323961.29 | Y
HOSPITAL | UAB-HOSPITAL | MEB | 0060 | MEDICAL EDUCATION BLDG | 26073.73 | 44315.14 | 49864.14 | Y
HOSPITAL | UAB-HOSPITAL | NHB | 0135 | NEW HILLMAN | 31567.61 | 50711.07 | 62416.07 | Y
HOSPITAL | UAB-HOSPITAL | NP | 0327 | NORTH PAVILION | 440842.07 | 753818.63 | 877155.63 | Y
HOSPITAL | UAB-HOSPITAL | NW | 0213 | NORTH WING | 64280.92 | 106513.06 | 122584.06 | Y
HOSPITAL | UAB-HOSPITAL | OHB | 0136 | OLD HILLMAN | 28055.17 | 37443.95 | 46080.95 | Y
HOSPITAL | UAB-HOSPITAL | OSB | 0424 | ORTHOPEDIC SPECIALTIES BUILDING | 19247.94 | 28040.09 | 31055.09 | Y
HOSPITAL | UAB-HOSPITAL | POB | 0423 | PHYSICIAN'S OFFICE BUILDING | 106334.89 | 123278.62 | 131402.62 | Y
HOSPITAL | UAB-HOSPITAL | QT | 0147 | QUARTERBACK TOWER | 43934.59 | 77557.82 | 92677.82 | Y
HOSPITAL | UAB-HOSPITAL | RWUH | 0148 | RUSSELL AMBULATORY CENTER | 40368.81 | 83121.28 | 93992.28 | Y
HOSPITAL | UAB-HOSPITAL | SRC | 0158 | SPAIN REHAB | 88096.56 | 134104.53 | 154652.53 | Y
HOSPITAL | UAB-HOSPITAL | SW | 0162 | SPAIN TOWER | 94227.02 | 159318.26 | 182417.26 | Y
HOSPITAL | UAB-HOSPITAL | TCF | 0163 | TRASH COMPACTOR | 23.75 | 1982.14 | 2262.14 | Y
HOSPITAL | UAB-HOSPITAL | HGLD | 0401 | UAB HIGHLANDS | 271561.52 | 422871 | 467679 | Y
HOSPITAL | UAB-HOSPITAL | WT | 0187 | WALLACE TOWER | 81044.86 | 132620.45 | 150718.45 | Y
HOSPITAL | UAB-HOSPITAL | WP | 0224 | WEST PAVILION | 161460.03 | 342151.73 | 388082.73 | Y
CAMPUS | UNIV OF ALABAMA AT BHAM | PD5A | 0347 | 5TH AVE PARKING DECK | 279919.27 | 287566.33 | 295161.33 | Y
CAMPUS | UNIV OF ALABAMA AT BHAM | PD6A | 0140 | 6TH AVENUE PARKING DECK | 535652.76 | 568919.11 | 593207.11 | Y
CAMPUS | UNIV OF ALABAMA AT BHAM | BDB | 0004 | BOSHELL BUILDING | 64928.83 | 111821.62 | 128765.62 | Y
CAMPUS | UNIV OF ALABAMA AT BHAM | CIRC | 0226 | CIVITAN BUILDING | 34361.61 | 52498.96 | 59145.96 | Y
CAMPUS | UNIV OF ALABAMA AT BHAM | LHFOT | 0351 | LYONS-HARRISON FACULTY OFFICE TOWER | 62055.61 | 90121.71 | 102732.71 | Y
CAMPUS | UNIV OF ALABAMA AT BHAM | WTI | 0188 | WALLACE TUMOR INSTITUTE | 85142.27 | 140405.38 | 159083.38 | Y

## 14. Required Documents
Required Documents
Document Name | Instructions
RFP AGREEMENT | A signed copy of the RFP document must be returned with your submission.
APPENDIX A (Vendor Disclosure Statement, VDS) | Complete the "Vendor Disclosure Statement" (attached to the RFP as Appendix A) and submit a signed copy with RFP response. Failure to provide this document will result in a non-award of the referenced products and/or services.
APPENDIX B (Certification of Compliance with Section Nine of Act 2011-535) | Complete the Certification of Compliance (attached to the RFP as Appendix B) and submit a signed copy with RFP response. Failure to provide this document will result in a non-award of the referenced products and/or services.
APPENDIX C (EXCEL DOCUMENT) | Please complete all sections of Appendix C in the excel document provided. An electronic copy of the completed excel document must be submitted with your RFP submission. Please do not put any password protections on the excel document. You may print out each section of the excel document and include a hard copy with your submission.
IMPLEMENTATION TIMELINE | Please submit an Implementation Timeline.
AGREEMENTS | All license agreements or contracts which must be signed prior to delivery of proposed products and/or service, must be included with the proposal response for review by the Hospital. It is expected that the terms of this RFP will supersede any additional terms of the Vendor. The terms and conditions of any additional agreements must align with the specifications, requirements and terms and conditions of this RFP.
WARRANTY TERMS | Any warranty terms, other than warranties established by the laws of the State of Alabama, must be explicitly provided in Vendor’s response. If applicable, please provide a copy of warranty terms.
VALUE ADDS | Vendors are encouraged to include additional “Value Propositions” or “Value Adds” which might be in the Hospital’s best interest. Please provide
ADDITIONAL DOCUMENTATION | It is the vendor’s sole responsibility to include in its response sufficient product literature, specifications, and other information necessary to completely describe the products and/or services being offered. All license agreements or, contracts, which must be signed prior to delivery of proposed service, must be included with the proposal for review by the Hospital.